## 12V Cmd list ver2
600w 12V PMBus Commands list
Command Code | PMBus 1.2 Sepc
|  | Page |  |  | Transaction type
| Command Name | 0(12V) | 1(5VSB) | Writing data | Reading data | No of Data Bytes | Default Value | Instruction
0x00 | PAGE | yes | yes | Write Byte | Read Byte | 1 | 00h | provides the ability to configure,control, and monitor multiple phases on one PMBus unit
0x01 | OPERATION | yes | yes | Write Byte | Read Byte | 1 | 80h | turn unit on or off in conjunction with the input from the control pin | Only supports Immediate Off and ON,
0x19 | CAPABILITY | yes | yes | N/A | Read Byte | 1 | 90h | determine some key capabilities of a PMBus device
0x1A | QUERY |  |  | Block Write- Block Read Process Call |  | Variable |  | ask a PMBus device if it supports a given command
0x20 | VOUT_MODE | yes | yes | N/A | Read Byte | 1 | 18h | whether the device uses the Linear, VID or Direct modes for output voltage related commands
0x3A | FAN_CONFIG_1_2 | yes | yes | N/A | Read Byte | 1 | 99h/90h | configure up to fan associated with one PMBus device(Default:No Fan)
0x3B | FAN_COMMAND_1 | yes | yes | Write Word | Read Byte | 2 | 0 | Set the value of duty and Get duty ; (self-defined command)
0x40 | VOUT_OV_FAULT_LIMIT | yes | yes | N/A | Read Byte | 2 | D80h | set the value of the output voltage at the sense or output pins that causes an output voltage high warning
0x46 | IOUT_OC_FAULT_LIMIT | yes | yes | Write Word | Read Word | 2 | F370h | set the value of the output current,in amperes, that causes the overcurrent detector to indicate an overcurrent fault condition
0x4A | IOUT_OC_WARN_LIMIT | yes | yes | Write Word | Read Word | 2 | F348h | set the value of the output current that causes an output overcurrent warning
0x4F | OT_FAULT_LIMIT | yes | yes | N/A | Read Word | 2 | MFR defined(006Eh),(0043h) | set the temperature, in degrees Celsius, of the unit at which it should indicate an Overtemperature
0x51 | OT_WARN_LIMIT | yes | yes | N/A | Read Word | 2 | MFR defined(0064h),(0037h) | set the temperature, in degrees Celsius, of the unit at which it should indicate an Undertemperature Warning alarm
0x78 | STATUS_BYTE | yes | yes | N/A | Read Byte | 1 |  | returns one bytes of information with a summary of the unit’s fault condition
0x79 | STATUS_WORD | yes | yes | N/A | Read Word | 2 |  | returns two bytes of information with a summary of the unit’s fault condition
0x7A | STATUS_VOUT | yes | yes | N/A | Read Byte | 1 |  | return one data byte with contents:Output Overvoltage Fault,Warning,Undervoltage Warning,Fault TON_MAX_FAULT,Fault TOFF_MAX_ WARNING,VOUT Tracking Error
0x7B | STATUS_IOUT | yes | yes | N/A | Read Byte | 1 |  | return one data byte with contents as follows:Output Overcurrent Fault,Output Overcurrent And Low Voltage Fault,Output Overcurrent Warning,Output Undercurrent Fault,Current Share Fault,In Power Limiting Mode,Output Overpower Fault,Output Overpower Warning
0x7C | STATUS_INPUT | yes | yes | N/A | Read Byte | 1 |  | returns one data byte with contents as follows:Input Overvoltage Fault,Input Overvoltage Warning,Input Undervoltage Warning,Input Undervoltage Fault,Unit Off For Insufficient Input Voltage,(Input Overcurrent Fault,Input Overcurrent Warning,Input Overpower Warning
0x7D | STATUS_TEMPERATURE | yes | yes | N/A | Read Byte | 1 |  | return one data byte with contents as follows:Overtemperature Fault,Overtemperature Warning,Undertemperature Warning,Undertemperature Fault
0x7E | STATUS_CML | yes | yes | N/A | Read Byte | 1 |  | returns one data byte with contents as follows:Invalid Or Unsupported Command Received,Invalid Or Unsupported Data Received,Packet Error Check Failed,Memory Fault Detected,Processor Fault Detected,A communication fault other than the ones listed in this table has occurred,Other Memory Or Logic Fault has occurred
0x7F | STATUS_OTHER | yes | yes | N/A | Read Byte | 1 |  | return one data byte with contents as follows:Input Fuse Or Circuit Breaker Fault,Input OR-ing Device Fault,Output OR-ing Device Fault
0x80 | STATUS_MFR_SPECIFIC | yes | yes | N/A | Read Byte | 1 |  | return one data byte with contents Manufacturer Defined
0x81 | STATUS_FANS_1_2 | yes | yes | N/A | Read Byte | 1 |  | report on the status of any fans installed in position 1
0x88 | READ_VIN | yes | yes | N/A | Read Word | 2 |  | return the input voltage in volts
0x8A | READ_VCAP | yes | yes | N/A | Read Word | 2 |  | return voltage on the energy storage capacitor in volts
0x8B | READ_VOUT | yes | yes | N/A | Read Word | 2 |  | return the actual, measured (not commanded) output voltage in the same format as set by the VOUT_MODE command
0x8C | READ_IOUT | yes | yes | N/A | Read Word | 2 |  | return the measured output current in amperes
0x8D | READ_TEMPERATURE_1 (Ambient) | yes | yes | N/A | Read Word | 2 |  | return the temperature in degree Celsius
0x8E | READ_TEMPERATURE_2 (Primary side) | yes | yes | N/A | Read Word | 2 |  | return the temperature in degree Celsius
0x8F | READ_TEMPERATURE_3 (Secondary side) | yes | yes | N/A | Read Word | 2 |  | return the temperature in degree Celsius
0x90 | READ_FAN_SPEED_1 | yes | yes | N/A | Read Word | 2 |  | fan speed(Defaul:0)
0x96 | READ_POUT | yes | yes | N/A | Read Word | 2 |  | return the output power, in watts, of the PMBus
0x98 | PMBUS_REVISION | yes | yes | N/A | Read Byte | 1 | 22h | store or read the revision of the PMBus to which the device is compliant
0xA0 | MFR_VIN_MIN | yes | yes | N/A | Read Word | 2 | 00B4h,00BEh | set or retrieve the minimum rated value, in volts, of the input voltage
0xA1 | MFR_VIN_MAX | yes | yes | N/A | Read Word | 2 | 0108h,0122h | set or retrieve the maximum rated value, in volts, of the input voltage
0xA2 | MFR_IIN_MAX | yes | yes | N/A | Read Word | 2 | D9D0h,DA20h | set or retrieve the maximum rated value, in amperes, of the input current
0xA3 | MFR_PIN_MAX | yes | yes | N/A | Read Word | 2 | 12B3h, 12ADh | set or retrieve the maximum rated Input power, in watts, that the unit is rated to supply
0xA4 | MFR_VOUT_MIN | yes | yes | N/A | Read Word | 2 | 0C20h | set or retrieve the minimum rated value, in volts, to which the output voltage may be set
0xA5 | MFR_VOUT_MAX | yes | yes | N/A | Read Word | 2 | 0CE0h | set or retrieve the maximum rated value, in volts, to which the output voltage may be set
0xA6 | MFR_IOUT_MAX | yes | yes | N/A | Read Word | 2 | F320h | set or retrieve the maximum rated value, in amperes, to which the output may be loaded
0xA7 | MFR_POUT_MAX | yes | yes | N/A | Read Word | 2 | 1271h | set or retrieve the maximum rated output power, in watts, that the unit is rated to supply
0xA8 | MFR_TAMBIENT_MAX | yes | yes | N/A | Read Word | 2 | 002Dh | set or retrieve the maximum rated ambient temperature, in degrees Celsius, in which the unit may be operated
0xA9 | MFR_TAMBIENT_MIN | yes | yes | N/A | Read Word | 2 | 0000h | set or retrieve the minimum rated ambient temperature, in degrees Celsius, in which the unit may be operated
0xD0 | MFR_FW_REVISION | yes | yes | N/A | Read Word | 1 | 23h | store or read the revision of the LiteOn FW to which the device is compliant | I2C Addr 0Xb4 OR 0X b6 in PS2252
0xD1 | MFR_Enable | yes | yes | Block Write- Block Read Process Call |  | 4 | 6e6f694ch | Factory Mode Enable Command S+AddrW+D1h+4ch+69h+6Fh+6Eh+P
0xBD | Calibration_Cmd | yes | yes | Block Write- Block Read | Block Write- Block Read Process Call | Variable | N/A |  | ask a PMBus device if it supports a given command
0xEA | Calibration_Save_En | yes | yes | Write Byte | Write Word | 1 | 0000h | Enable (9Ah)/Disable (56h) the calibration Save Command

## Calibration cmd
Sub Cmd
| clear All | 01 02
| Write with Index | 08 00
| Write with Index | 02 01
Calibration data index
| Vin Reporting | 0
| Reserved | 1
| Reserved | 2
| Iin Reporting Low#1 | 3
| Iin Reporting Low#2 | 4
| Reserved | 5
| Iin Reporting High#1 | 6
| Iin Reporting High#2 | 7
| Reserved | 8
| PIin Reporting Low#1 | 9
| Pin Reporting Low#2 | 0x0A
| Reserved | 0xB
| Pin Reporting High#1 | 0xC
| PIin Reporting High#2 | 0xD
| Reserved | 0xE
| Reserved | 0xF
| Vout Setpoint | 0x10
| Vout Reporting | 0x11
| Reserved | 0x12
| Iout Reporting #1 | 0x13
| Iout Reporting #2 | 0x14
| Reserved | 0x15
| Reserved | 0x16
| DroopRef | 0x17
| Reserved | 0x18
| Reserved | 0x19

## Status
2. Status detail definition
Status | Bit | Name | Comments | Required | PAGE0 Status | PAGE1 Status
Status_Word Low | 7 | BUSY |  | useless
| 6 | OFF | This bit is asserted if the unit is not providing power to the output, regardless of the reason, including simply not being enabled. | yes | Recover | Recover
| 5 | VOUT_OV | An output overvoltage fault has occurred | yes | Latch | Recover
| 4 | IOUT_OC | An output overcurrent fault has occurred | yes | Latch | N/A
| 3 | VIN_UV | An input undervoltage fault has occurred | yes | Recover | Recover
| 2 | TEMPERATURE | A temperature fault or warning has occurred | yes | Latch | Latch
| 1 | CML | A communications, memory or logic fault has occurred | yes | Latch | N/A
| 0 | NONE OF THE ABOVE | A fault or warning not listed in bits [7:1] of this byte has occurred | useless
Status_Word High | 7 | VOUT | An output voltage fault or warning has occurred | yes | Latch | Recover
| 6 | IOUT/POUT | An output current or output power fault or warning has occurred | yes | Latch | N/A
| 5 | INPUT | An input voltage, input current, or input power fault or warning has occurred | yes | Recover | Recover
| 4 | MFR |  | useless
| 3 | POWER_GOOD# | The POWER_GOOD signal, if present, is negated¹ | yes | Recover | Recover
| 2 | FANS | A fan or airflow fault or warning has occurred | yes | Latch | N/A
| 1 | OTHER |  | useless
| 0 | UNKNOWN | A fault type not given in bits [15:1] of the SATUS_WORD has been detected | useless
Status_Input | 7 | VIN_OV_FAULT | Input Overvoltage Fault | yes | Recover | Recover
| 6 | VIN_OV_WARN | Input Overvoltage Warning | yes | Recover | Recover
| 5 | VIN_UV_WARN | Input Undervoltage Warning | yes | Recover | Recover
| 4 | VIN_UV_FAULT | Input Undervoltage Fault) | yes | Recover | Recover
| 3 | Unit Off For Insufficient Input Voltage | Either the input voltage has never exceeded the input turn-on threshold (Section14.5) or if the unit did start, the input voltage decreased below the turn-off threshold | yes | Recover | Recover
| 2 | IIN_FAULT |  | useless
| 1 | IIN_WARN |  | useless
| 0 | PIN_WARN |  | useless
Status_Vout | 7 | VOUT_OV_FAULT | Output Overvoltage Fault | yes | Latch | Recover
| 6 | VOUT_OV_WARN | Output Overvoltage Warning | yes | Latch | Recover
| 5 | VOUT_UV_WARN | Output Undervoltage Warning | yes | Latch | Recover
| 4 | VOUT_UV_FAULT | Output Undervoltage Fault | useless
| 3 | VOUT_MAX_WARN | An attempt has been made to set the output voltage to value higher than allowed by the VOUT_MAX command | useless
| 2 | TON_MAX_FAULT |  | useless
| 1 | TOFF_MAX_WARN |  | useless
| 0 | VOUT_TRACK_ERROR |  | useless
Status_Iout | 7 | IOUT_OC_FAULT | Output Overcurrent Fault | yes | Latch | Recover
| 6 | IOUT_OC_LV_FAULT |  | useless
| 5 | IOUT_OC_WARN | Output Overcurrent Warning | yes | Latch | Recover
| 4 | IOUT_UC_FAULT |  | useless
| 3 | Current_share_FAULT |  | useless
| 2 | Power_LIMIT |  | useless
| 1 | POUT_OVERPOWER_FAULT |  | useless
| 0 | POUT_OVERPOWER_WARN |  | useless
Status_Temperature | 7 | OT_FAULT | Overtemperature Fault | yes | Latch | Latch
| 6 | OT_WARN | Overtemperature Warning | yes | Latch | Latch
| 5 | UT_WARN |  | useless
| 4 | UT_FAULT |  | useless
| 3 | Reserved |  | useless
| 2 | Reserved |  | useless
| 1 | Reserved |  | useless
| 0 | Reserved |  | useless
Status_Fans_1_2 | 7 | FAN1_FAULT | these bits are set if the fan has failed completely or is simply not able to provide the minimum RPM needed to cool the device or system in which it is embedded. | yes | Latch | N/A
| 6 | FAN2_FAULT | as above | yes | Latch | N/A
| 5 | FAN1_WARN |  | useless
| 4 | FAN2_WARN |  | useless
| 3 | FAN1_OVER-RIDE |  | yes | Latch | N/A
| 2 | FAN2_OVER-RIDE |  | yes | Latch | N/A
| 1 | AIRFLOW_FAULT |  | useless
| 0 | AIRFLOW_WARN |  | useless
Status_Other | 7 | reserved |  | useless
| 6 | reserved |  | useless
| 5 | INA_BRK_FAULT |  | useless
| 4 | INB_BRK_FAULT |  | useless
| 3 | INA_OR_FAULT |  | useless
| 2 | INB_OR_FAULT |  | useless
| 1 | OUT_OR_FAULT |  | useless
| 0 | reserved |  | useless
Status_CML | 7 | INVALID_CMD | Invalid Or Unsupported Command Received | yes | Latch | N/A
| 6 | INVALID_DATA | Invalid Or Unsupported Data Received | yes | Latch | N/A
| 5 | PEC_FAULT | Packet Error Check Failed | yes | Latch | N/A
| 4 | MEM_FAULT |  | useless
| 3 | CPU_FAULT |  | useless
| 2 | reserved |  | useless
| 1 | OTHER_FAULT | A communication fault other than the ones listed in this table has occurred. Refer to 10.8. Data Transmission Faults | yes | Latch | N/A
| 0 | MEM_LOGIC_FAULT |  | useless

## Revision
Version | Description | Date | By
1 | Initial release | 2021-02-21
1.01 | remove some command based on delta reference | 2021-05-11
1.02 | Add calibration command based on liteon ps2251 reference | 2021-06-08

## AWS Black Box Log
MFR_PAGE(0XE4)
MFR_PAGE | Refers to | Comments
0XFF | Real time data (default value) | When a fault condition occurs, the PSU must save certain status registers into non-volatile memory. The PSU must save a record of this data for the last five fault events. The history will be accessed via the MFR_PAGE command (E4h). If the history fills up, delete the oldest record and shift the remaining records down the queue following FIFO. Up to 17 black box events can be recorded.
0X00 | Fault history 1 (newest fault event)
0X01 | Fault history 2
0X02 | Fault history 3
0X03 | Fault history 4
0X04 | Fault history 5
0X05 ~0X10 | Option additional fault history locations
Sensors to save upon each fault event table
Command Number | Command Name | Command Number | Command Name
0x79 | STATUS_WORD | 0x8D | READ_TEMPERATURE_1 (Ambient)
0x7A | STATUS_VOUT | 0x8E | READ_TEMPERATURE_2 (Primary side)
0x7B | STATUS_IOUT | 0x8F | READ_TEMPERATURE_3 (Secondary side)
0x7C | STATUS_INPUT | 0x90 | READ_FAN_SPEED_1
0x7D | STATUS_TEMPERATURE | 0x96 | READ_POUT
0x7E | STATUS_CML | 0x97 | READ_PIN
0x81 | STATUS_FANS_1_2 | 0xD0 | MFR_FW_REVISION
0x88 | READ_VIN
0x89 | READ_IIN
0x8B | READ_VOUT
0x8C | READ_IOUT
Log fetch
1. Write Byte to CMD 0X10 ->WRITE_PROTECT Disable -> 0x00
2. Write Byte to CMD 0XE4 -> Fault history 1 (newest fault event) -> 0x00
3. Read Black Box event log -> Read fault event 1 table, EX: read cmd 0x79~7E,..etc.
4. If you want to read other older fault events, change the value from item 2, for example: Fault history 2 -> 0x01
5. Write Byte to CMD 0XE4 -> 0XFF -> Real time data (default value). Expressed as the current information, there is no black box fault event.

## FRU Data Format
OFFSET |  | DEFINITION | SPEC VALUE
|  | (REMARKS) | dec | hex
COMMON HEADER, 8 bytes
000d | 00h | Format Version Number (Common Header) | 1 | 1
001d | 01h | Internal Use Area Offset (In multiples of 8 Bytes),NOT APPLICABLE | 0 | 0
002d | 02h | Chassis Info Area Offset (In multiples of 8 Bytes),NOT APPLICABLE | 0 | 0
003d | 03h | Board Info Area Offset (Not Used) | 0 | 0
004d | 04h | Product Info Area Offset (In multiples of 8 Bytes) | 22 | 16
005d | 05h | Multi Record Area Offset (In multiples of 8 Bytes),NOT APPLICABLE | 0 | 0
006d | 06h | PAD (reserved – always 00H) | 0 | 0
007d | 07h | Zero Check Sum (256 – (Sum of bytes 000d to 006d)) | 233 | E9
MULTI RECORD AREA : Power Supply Information 72 Bytes
Power Supply Record Header
08d | 08h | Record Type ID (0x00 = Power Supply Information) | 0 | 0
09d | 09h | 7: (1)b, End of List 6-4: (000)b, Reserved 3-0: (0010)b, Record Format Version | 0 | 0
010d | 0Ah | Record Length: 24 Bytes | 0 | 0
011d | 0Bh | Record Checksum (Zero Checksum From 013d To 036d ) | 0 | 0
012d | 0Ch | Header Checksum (Zero Checksum From 008d To 011d) | 0 | 0
Power Supply Record
013d | 0Dh | Overall Capacity1_LB (Watts) 15-12: (0000)b, Reserved 11-0: (000000000000)b, 0W Stored with LSB first then MSB. | 0 | 0
014d | 0Eh | Overall Capacity2_HB (Watts) | 0 | 0
015d~016d | 0Fh~10h | Peak VA (Watts) 15-12: (0000)b, Reserved 11-0: No peak VA rating Stored with LSB first then MSB. | 0 | 0
017d | 11h | Inrush Current (Amps), 00Amps | 0 | 0
018d | 12h | Inrush Interval (ms), 0ms | 0 | 0
019d~020d | 13h~14h | Low End Input Voltage Range 1 | 0 | 0
021d~022d | 15h~16h | High End Input Voltage Range 1 | 0 | 0
023d | 17h | Low End Input Voltage Range 2-LB 0V = 0 (0x10mV) Stored with LSB first then MSB. | 0 | 0
024d | 18h | Low End Input Voltage Range 2-HB | 0 | 0
025d | 19h | High End Input Voltage Range 2-LB 0V = 0 (0x10mV) Stored with LSB first then MSB. | 0 | 0
026d | 1Ah | High End Input Voltage Range 2-HB | 0 | 0
027d | 1Bh | Low End Input Frequency Range, 0Hz | 0 | 0
028d | 1Ch | High End Input Frequency Range, 0Hz | 0 | 0
029d | 1Dh | A/C Dropout Tolerance in ms, 0ms | 0 | 0
030d | 1Eh | Binary Flags 7-5: (000)b, Reserved 4: (1)b, Tachometer Puls es per Rotation / Predictive Fail Polarity (2 Pulses Per Rotation = 1; 1 Pulse Per Rotation = 0) OR (Signal Asserted(1) Indicates Failure = 0, Signal Deasserted(0) Indicates Failure = 1) 3: (0)b, Hot Swap / Redundancy Support 2: (0)b, AutoSwitch Support 1: (0)b, Power Factor Correction Support 0: (0)b, Predictive Fail Support | 0 | 0
031d~032d | 1Fh~20h | Peak Wattage Capacity and Holdup Time, 15-12: (0000)b, Hold Up Time in Seconds = 00H (Not Specified), 11-0: (000000000000)b, Peak Capacity in Watts = 00H (Not Specified) | 0 | 0
033d~035d | 21h~23h | Combined Wattage, NOT APPLICABLE | 0 | 0
036d | 24h | Predictive Fail Tachometer Lower Threshold, Not applicable | 0 | 0
037d~079d | 25h~4Fh | MULTI RECORD AREA, NOT APPLICABLE | 0 | 0
INTERNAL USE AREA, 64 bytes
080d | 50h | INTERNAL USE AREA Format Version Number 7:4 -reserved, write as 0000b 3:0 -format version number = 1h for this specification. | 0 | 0
081d~142d | 51h~8Eh | NOT APPLICABLE | 0 | 0
143d | 8Fh | Zero Checksum (256 – (Sum of bytes 080d to 142d)) | 0 | 0
CHASSIS INFORMATION AREA, 32 bytes
144d | 90h | Format Version Number (Default value is 1.) | 0 | 0
145d | 91h | Chassis Info Area Length (Default value is 0.) | 0 | 0
146d | 92h | Chassis Type (Default value is 0.) | 0 | 0
147d | 93h | Chassis Part Number Type/Length 10 byte allocation 0CAH (if used) (Default value is 0.) | 0 | 0
148d~157d | 94h~9Dh | Chassis Part Number (Default value is 0.) | 0 | 0
158d | 9Eh | Chassis Serial Number Type/Length 15 byte allocation 0CFH (if used) (Default value is 0.) | 0 | 0
159d~173d | 9Fh~ADh | Chassis Serial Number (Default value is 0.) | 0 | 0
174d | AEh | End Tag (0C1H if used) (Default value is 0.) | 0 | 0
175d | AFh | Zero Check Sum (256 – (Sum of bytes 144d to 174d)) | 0 | 0
Product Info Area Format, 80 bytes
176d | B0h | Product Area Format Version Number | 1 | 1
177d | B1h | Product Info Area Length (In multiple of 8 bytes) 80 Bytes are allocated. 80-Bytes / 8 = 0AH. | 10 | A
178d | B2h | Language, English = 19H | 25 | 19
179d | B3h | Manufacturer Name Type/Length (0C5H) 7-6: (11)b, 8-Bit ASCII + Latin 1, 5-0: (000110)b, 6-Byte Allocation | 198 | C6
180d | B4h | Manufacturer Name 1, 'L' | 76 | 4C
181d | B5h | Manufacturer Name 2, 'I' | 73 | 49
182d | B6h | Manufacturer Name 3, 'T' | 84 | 54
183d | B7h | Manufacturer Name 4, 'E' | 69 | 45
184d | B8h | Manufacturer Name 5, 'O' | 79 | 4F
185d | B9h | Manufacturer Name 6, 'N' | 78 | 4E
186d | BAh | Product Name Type/Length (0CEH) 7-6: (11)b, 8-Bit ASCII + Latin 1, 5-0: (010000)b, 16-Byte Allocation | 208 | D0
187d | BBh | Product Name 1, 'P' | 80 | 50
188d | BCh | Product Name 2, 'S' | 83 | 53
189d | BDh | Product Name 3, '-' | 45 | 2D
190d | BEh | Product Name 4, '1' | 49 | 31
191d | BFh | Product Name 5, '6' | 54 | 36
192d | C0h | Product Name 6, '0' | 48 | 30
193d | C1h | Product Name 7, '3' | 51 | 33
194d | C2h | Product Name 8, '-' | 45 | 2D
195d | C3h | Product Name 9, 'x' | 120 | 78
196d | C4h | Product Name 10, '0' | 48 | 30
197d | C5h | Product Name 11, '1' | 49 | 31
198d | C6h | Product Name 12, ' ' | 32 | 20
199d | C7h | Product Name 13, ' ' | 32 | 20
200d | C8h | Product Name 14, ' ' | 32 | 20
201d | C9h | Product Name 15, ' ' | 32 | 20
202d | CAh | Product Name 16, ' ' | 32 | 20
203d | CBh | Part/Model Number Type/Length (0CAH) 7-6: (11)b, 8-Bit ASCII + Latin 1, 5-0: (010000)b, 16-Byte Allocation | 208 | D0
204d~219d | CCh~DBh | Power Supply Spare Kit Number NOT APPLICABLE | 0 | 0
220d | DCh | Product Version Number Type/Length (0C2H) 7-6: (11)b, 8-Bit ASCII + Latin 1, 5-0: (000010)b, 2-Byte Allocation | 194 | C2
221d | DDh | Product Version Number1 / Auto Rev, 'X' | 88 | 58
222d | DEh | Product Version Number2 / Auto Rev, '3' | 51 | 33
223d | DFh | Product Serial Number Type/Length (0CDH) *PRODUCT SERIAL NUMBER P/N: 6XXXX01RRYWWXXX, EX:66A1U01X3G5022X 7-6: (11)b, 8-Bit ASCII + Latin 1, 5-0: (010000)b, 16-Byte Allocation | 208 | D0
224d | E0h | Product Serial Number1, COMMODITY CODE, '6' | 54 | 36
225d | E1h | Product Serial Number2~5, XXXX-> PROJECT CODE (PS-RRRR-XXXX), EX:PS-2252-6A1U Product Serial Number2, '6' | 54 | 36
226d | E2h | Product Serial Number3, 'A' | 65 | 41
227d | E3h | Product Serial Number4, '1' | 49 | 31
228d | E4h | Product Serial Number5, 'U' | 85 | 55
229d | E5h | Product Serial Number6~7, 01-> SITE/VENDOR CODE (01), Product Serial Number6, '0' | 48 | 30
230d | E6h | Product Serial Number7, '1' | 49 | 31
231d | E7h | Product Serial Number8~9, RR-> CUSTOMER REVISION(X3), Product Serial Number8, 'X' | 88 | 58
232d | E8h | Product Serial Number9, '3' | 51 | 33
233d | E9h | Product Serial Number10, Y-> LAST NUMBER OF YEAR (G=2016…) Product Serial Number10, 'G' | 71 | 47
234d | EAh | Product Serial Number11~12, WW-> WEEK (01~52) Product Serial Number11, '5' | 53 | 35
235d | EBh | Product Serial Number12, '0' | 48 | 30
236d | ECh | Product Serial Number13~15, XXX-> SEQUENCE NUMBER (001~ZZZ) Product Serial Number13, '2' | 50 | 32
237d | EDh | Product Serial Number14, '2' | 50 | 32
238d | EEh | Product Serial Number15, 'X' | 88 | 58
239d | EFh | Product Serial Number16, ' ' | 32 | 20
240d | F0h | ASSET TAG 7-6: (11)b, 8-Bit ASCII + Latin 1, 5-0: (001000)b, 8-Byte Allocation | 200 | C8
241d~248d | F1h~F8h | NO ASSET TAG | 0 | 0
249d | F9h | FRU File ID 7-6: (11)b, 8-Bit ASCII + Latin 1, 5-0: (000100)b, 4-Byte Allocation | 196 | C4
250d~253d | FAh~FDh | “Should track latest EEPROM Revision on IPS Sec. 1.2” NOT APPLICABLE | 0 | 0
254d | FEh | End of Fields Marker | 193 | C1
255d | FFh | Zero Checksum (256 – (Sum of bytes 176d to 254d)) | 85 | 55

## FRU DATA TABLE
FRU DATA TBALE
| 00 | 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 0A | 0B | 0C | 0D | 0E | 0F
00 | 01 | 00 | 00 | 00 | 16 | 00 | 00 | E9 | 0 | 00 | 00 | 00 | 00 | 00 | 00 | 00
10 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
20 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
30 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
40 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
50 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
60 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
70 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
80 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
90 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
A0 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
B0 | 1 | 0A | 19 | C6 | 4C | 49 | 54 | 45 | 4F | 4E | D0 | 50 | 53 | 2D | 32 | 32
C0 | 35 | 32 | 2D | 36 | 41 | 31 | 55 | 20 | 20 | 20 | 20 | D0 | 00 | 00 | 00 | 00
D0 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | C2 | 58 | 33 | D0
E0 | 36 | 36 | 41 | 31 | 55 | 30 | 31 | 58 | 33 | 47 | 35 | 30 | 32 | 32 | 58 | 20
F0 | C8 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | C4 | 00 | 00 | 00 | 00 | C1 | 55
Note:. 1.A total of 15 bar codes are written to the address block 0xE0. EX:66A1U01X3G5022X

## Reference DOC
3. Reference
1 | PMBus_Specification_Part_II_Rev_1-2_20100906
2 | System Management Bus(SMBus)Specification V2.0
3 | Appnotes_IMA_X600-12, Delta